## Slide 1
Open‑Source Modular Architecture for Grid Intelligence Using Linux-Native Infrastructure
Dr. Nikita Ramachandra, Project Officer (Former), IIT Madras
Dr. Satabdy Jena, Power Systems Modeling Researcher, Shell India Markets Pvt. Ltd.
Notes: Hello Everyone! Power system networks are no longer passive systems. With global decarbonisations efforts, the share of renewables in the energy mix is increasing and therefore, power distribution systems are becoming active, data-rich, and operationally complex. The question is no longer whether we need advanced grid intelligence, but how we can deploy it in a scalable, interoperable, and accessible way. In this session we will present an open-source blueprint for doing exactly that—(using Linux-based containers, Kubernetes orchestration, time-series data platforms, and modular power-system services that can be independently developed, validated, and scaled.) But before we delve deeper into that –- (transition to next slide) –

## Slide 2: Cautionary Note
The companies in which Shell plc directly and indirectly owns investments are separate legal entities. In this content “Shell”, “Shell Group” and “Group” are sometimes used for convenience to reference Shell plc and its subsidiaries in general. Likewise, the words “we”, “us” and “our” are also used to refer to Shell plc and its subsidiaries in general or to those who work for them. These terms are also used where no useful purpose is served by identifying the particular entity or entities. ‘‘Subsidiaries’’, “Shell subsidiaries” and “Shell companies” as used in this content refer to entities over which Shell plc either directly or indirectly has control. The terms “joint venture”, “joint operations”, “joint arrangements”, and “associates” may also be used to refer to a commercial arrangement in which Shell has a direct or indirect ownership interest with one or more parties. The term “Shell interest” is used for convenience to indicate the direct and/or indirect ownership interest held by Shell in an entity or unincorporated joint arrangement, after exclusion of all third-party interest.
Forward-Looking statements
This content contains forward-looking statements (within the meaning of the U.S. Private Securities Litigation Reform Act of 1995) concerning the financial condition, results of operations and businesses of Shell. All statements other than statements of historical fact are, or may be deemed to be, forward-looking statements. Forward-looking statements are statements of future expectations that are based on management’s current expectations and assumptions and involve known and unknown risks and uncertainties that could cause actual results, performance or events to differ materially from those expressed or implied in these statements. Forward-looking statements include, among other things, statements concerning the potential exposure of Shell to market risks and statements expressing management’s expectations, beliefs, estimates, forecasts, projections and assumptions. These forward-looking statements are identified by their use of terms and phrases such as “aim”; “ambition”; ‘‘anticipate’’; “aspire”, “aspiration”, ‘‘believe’’; “commit”; “commitment”; ‘‘could’’; “desire”; ‘‘estimate’’; ‘‘expect’’; ‘‘goals’’; ‘‘intend’’; ‘‘may’’; “milestones”; ‘‘objectives’’; ‘‘outlook’’; ‘‘plan’’; ‘‘probably’’; ‘‘project’’; ‘‘risks’’; “schedule”; ‘‘seek’’; ‘‘should’’; ‘‘target’’; “vision”; ‘‘will’’; “would” and similar terms and phrases. There are a number of factors that could affect the future operations of Shell and could cause those results to differ materially from those expressed in the forward-looking statements included in this content, including (without limitation): (a) price fluctuations in crude oil and natural gas; (b) changes in demand for Shell’s products; (c) currency fluctuations; (d) drilling and production results; (e) reserves estimates; (f) loss of market share and industry competition; (g) environmental and physical risks, including climate change; (h) risks associated with the identification of suitable potential acquisition properties and targets, and successful negotiation and completion of such transactions; (i) the risk of doing business in developing countries and countries subject to international sanctions; (j) legislative, judicial, fiscal and regulatory developments including tariffs and regulatory measures addressing climate change; (k) economic and financial market conditions in various countries and regions; (l) political risks, including the risks of expropriation and renegotiation of the terms of contracts with governmental entities, delays or advancements in the approval of projects and delays in the reimbursement for shared costs; (m) risks associated with the impact of pandemics, regional conflicts, such as the Russia-Ukraine war and the conflict in the Middle East, and a significant cyber security, data privacy or IT incident; (n) the pace of the energy transition; and (o) changes in trading conditions. No assurance is provided that future dividend payments will match or exceed previous dividend payments. All forward-looking statements contained in this content are expressly qualified in their entirety by the cautionary statements contained or referred to in this section. Readers should not place undue reliance on forward-looking statements. Additional risk factors that may affect future results are contained in Shell plc’s Form 20-F for the year ended December 31, 2025 (available at www.shell.com/investors/news-and-filings/sec-filings.html and www.sec.gov). These risk factors also expressly qualify all forward-looking statements contained in this content and should be considered by the reader. Each forward-looking statement speaks only as of the date of this content [17/06/2026]. Neither Shell plc nor any of its subsidiaries undertake any obligation to publicly update or revise any forward-looking statement as a result of new information, future events or other information. In light of these risks, results could differ materially from those stated, implied or inferred from the forward-looking statements contained in this content.
Shell’s net carbon intensity
Also, in this content we may refer to Shell’s “net carbon intensity” (NCI), which includes Shell’s carbon emissions from the production of our energy products, our suppliers’ carbon emissions in supplying energy for that production and our customers’ carbon emissions associated with their use of the energy products we sell. Shell’s NCI also includes the emissions associated with the production and use of energy products produced by others which Shell purchases for resale. Shell only controls its own emissions. The use of the terms Shell’s “net carbon intensity” or NCI is for convenience only and not intended to suggest these emissions are those of Shell plc or its subsidiaries.
Shell’s net-zero emissions target
Shell’s operating plan and outlook are forecasted for a three-year period and ten-year period, respectively, and are updated every year. They reflect the current economic environment and what we can reasonably expect to see over the next three and ten years. Accordingly, the outlook reflects our combined Scope 1 and 2 target, NCI target and our oil products ambition over the next ten years. However, Shell’s operating plan and outlook cannot reflect our 2050 net-zero emissions target, as this target is outside our planning period. Such future operating plans and outlooks could include changes to our portfolio, efficiency improvements and the use of carbon capture and storage and carbon credits. In the future, as society moves towards net-zero emissions, we expect Shell’s operating plans and outlooks to reflect this movement. However, if society is not net zero in 2050, as of today, there would be significant risk that Shell may not meet this target.
Forward-Looking non-GAAP measures
This content may contain certain forward-looking non-GAAP measures such as free cash flow and underlying operational expenses. We are unable to provide a reconciliation of these forward-looking non-GAAP measures to the most comparable GAAP financial measures because certain information needed to reconcile those non-GAAP measures to the most comparable GAAP financial measures is dependent on future events some of which are outside the control of Shell, such as oil and gas prices, interest rates and exchange rates. Moreover, estimating such GAAP measures with the required precision necessary to provide a meaningful reconciliation is extremely difficult and could not be accomplished without unreasonable effort. Non-GAAP measures in respect of future periods which cannot be reconciled to the most comparable GAAP financial measure are calculated in a manner which is consistent with the accounting policies applied in Shell plc’s consolidated financial statements.
The contents of websites referred to in this content do not form part of this content.
We may have used certain terms, such as resources, in this content that the United States Securities and Exchange Commission (SEC) strictly prohibits us from including in our filings with the SEC. Investors are urged to consider closely the disclosure in our Form 20-F, File No 1-32575, available on the SEC website www.sec.gov
.
Notes: “Please do not base your investment decisions on what we speak today.”

## Slide 3: Open Source Grid Intelligence for Modern Power Grids
Modern power systems are undergoing rapid transformation due to large scale adoption of renewable energy integration, increasing electrification, energy demands, & energy security.
Challenges exist!  Congestion, requirements for flexibility, Instability, poor observability
Need for more dynamic, decentralized, and data-intensive operation A ‘smarter’ grid.
Requirement of open source grid automation that can be adopted, validated, and scaled by utilities, industry partners, start-ups.
Reduce dependency on proprietary energy management systems.
Fig. Visualization of RES dominated power system networks, complex behavior of loads and evolving edge-intelligence
Figure courtesy: Microsoft Copilot
Notes: So, as we said that power grids are evolving at a faster pace due to wide-spread adoption of renewables, on account of nations focusing on reducing their carbon emissions, enhancing energy security, transitioning to EVs . Nevertheless, there are also challenges like grid congestion, requiring assets to be more flexible, vulnerability to go into instability and poor observability because of the numerous generation sources and offtake points. but conventional grids were not designed for this level of dynamism and their infrastructure needs a complete overhaul. The requirement is to revisit the grid automation architecture and innovate and most importantly share -- so that it can be adopted, validated and scaled by utilities , industry partners, start-ups. This also reduces the dependency on proprietary management systems.

## Slide 4: Transitioning from SOA to Modular Microservices
Traditional SCADA  Service oriented architecture (SOA).
But, Power-electronics–driven systems are changing how grids behave and are controlled.
Faster fault detection, isolation and recovery capabilities.
Future grid operation is expected to evolve toward more digital, interconnected, and intelligent architectures.
Fig. Grids at every stage need to be interconnected, digitized and intelligent.
Figure courtesy: Microsoft Copilot
Notes: Now, speaking of grid architecture – traditional grid scheduling control systems were based on Service Oriented Architectures (soa) . But they are inacapable of meeting the evolving system requirements owing to their coarse-grained, monolithic structure. Further, the higher penetration of power electronics based RES is changing the way grids behaved traditionally. Now we need mechanisms to detect faults faster, have isolation from the faulty part of the grid faster and also equally fast to re-connect back. The evolved requirements call forth the need for digitized and interconnected power systems with improved fault detection, isolation, and recovery mechanisms that enhance grid resilience. he remedy is to gradually transition the grid functionalities present in today’s classical Supervisory Control and Data Acquisition (SCADA) systems, which are SOA-based, to modular microservices-based control software solutions. And therefore to support scalable modernization, we would like to introduce a production-oriented open-source architecture that unifies key grid-intelligence functions as independently deployable microservices.

## Slide 5: SOGNO & Microservices Architecture
SOGNO:Service-based open-source grid automation platform for network operation
An initiative under Linux Foundation Energy focused on: Open-source grid automation, Cloud-native deployment, Interoperability and Scalable microservices-based grid applications.
SOGNO is based on international data standards such as CIM IEC61970 and IEC61850 to support interoperability in a broader sense.
Links : SOGNO - LF Energy
Service Oriented Grid for the Network of the Future | SOGNO energy
Independent deployment services | API-driven communication | Loose coupling | Scalable architecture | Faster updates and maintenance
PROPOSED MICROSERVICES APPROACH
Docker | Kubernetes | REST APIs | MQTT | Prometheus & Grafana
CORE TECHNOLOGIES
Functionalities and structure of Microservices , docker & Kubernetes
Figure courtesy: Microsoft Copilot, SOGNO Website, Google Images
Notes: It is not that we are thinking about it for the first time.. SOGNO in Italian meaning ‘dream’ is a global initiative under the Linux Foundation Energy which is a part of European Union’s Horizon 2020 research. The vision is to integrate today’s SCADA systems with SOGNO and then to gradually move functionalities into microservices. Therefore, SOGNO is not in opposition to classical solutions but it can be seen as an add-on that supports a flexible growth of the automation architecture. This allows operators to adapt faster with components that can be updated independently from each other while recognizing the “brown field” that most utilities continue to operate in. SOGNO provides system operators and automation software developers a pathway to the future through an open source framework that exposes open APIs that plug-in new automation functions, while supporting industry standards such as CIM IEC61970.

## Slide 6: The SOGNO Services SOGNO Baseline vs. Custom Developed Modules
Architectural Layer | Module Name | Origin
Layer 0: Data & Foundation | Network Topology Processor (NTP) | Custom Developed
Layer 1: Core Analytics & Monitoring | Load & Generation Forecasting (LGF) | SOGNO Core
 | Power Quality Evaluation (PQE) | SOGNO Core
 | State Estimation (SE) | SOGNO Core
 | Online Load Flow | Custom Developed
Layer 2: Active Grid Control | Power Control (PC) | SOGNO Core
 | EnVVARCO | Custom Developed
 | Network Reconfiguration | Custom Developed
Layer 3: Automation & Self-Healing | FLISR | SOGNO Core (Under Development)
 | Fault Location | Custom Developed
 | Service Restoration | Custom Developed
 | Auto Recloser | Custom Developed
Notes: The first tranche of automation applications included– state estimation, load forecasting, voltage control. And thus, if we take a look at the

## Slide 7: Grid Automation Functionalities(GAFs) & their interconnectedness
Fig. Major Grid Automation Services and their interconnected nature
RESEARCH GAPS IDENTIFIED
 | Partial grid automation functionalities
 | Limited inter-module integration
 | No unified benchmark validation
 | Autonomous fault module unavailable
Notes: I would like to introduce the Grid Automation Services or otherwise known as GAFs. Broadly they are categorized into Energy Management Systems and Control tasks. EMS consists of PLF, SE NTP, OPF , DC-OPF. Control Tasks denotes the control of equipments connected to the network and how they are controlled to fulfil two major objectives of maintaining the system rated voltage and frequency within the allowed limits of variation. They include VVCO, CSC, VRC, TTC , NR SR and AR.

## Slide 8: The final picture: GAFs in SOGNO
Figure courtesy: Microsoft Copilot, SOGNO Website, Google Images
Notes: This slide is heavy . But I will walk you through the important components…(explain) This picture shows how the SOGNO platform supports real-time monitoring, analysis, optimization, and self-healing operation of a distribution grid. Data from field sensors such as voltage , current is collected through InfluxDB, processed by several grid-analysis services such as power flow, state estimation, topology processing, load forecasting, and optimal power flow, and then used by control applications such as Volt-VAR control, network reconfiguration, auto reclosing, and service restoration.
The key idea is that the platform is decentralized and modular: each function runs as an independent containerized service, usually through Docker, and the services exchange data and commands through a common communication network.
in next slides we will go through the modules one-by-one.

## Slide 9: Probabilistic Load Forecasting in SOGNO
Probabilistic load forecasting (PLF) is a method used to predict future electricity demand while accounting for the inherent uncertainties in the forecasting process.
ProLoaf module: enabling DSOs to operate DER-heavy distribution grids with better risk awareness, open interfaces, and cloud/edge-native deployment.
Fig. Fan chart examples for ProLoaf module functioning
Figure courtesy: Microsoft Copilot
Notes: We will go through the Proloaf module which is the is a probabilistic load forecasting project in SOGNO.

## Slide 10: Power Flow & State Estimation in SOGNO
Power flow analysis and state estimation are critical components in the operation and management of electrical power systems.
PyVolt -- The power flow analysis module provides voltage magnitudes and phase angles, along with branch power flows and nodal power injections. This helps to establish the initial steady-state operating point for the state estimations.
Fig. Power Flow and State Estimation running as pods in Kubernetes

## Slide 11: Designed NTP :Converting Grid Topology into Actionable Digital Intelligence
Network Topology Processor (NTP) is developed as a dedicated module to provide a detailed, machine-readable, and dynamically updatable representation of the distribution network.
A fundamental prerequisite for reliable monitoring, analysis, and control of modern distribution systems.
By transforming standardized CIM/XML descriptions into a coherent and computation-ready network model, NTP enables a consistent and computation-ready representation as demonstrated on the benchmark CIGRE system.
Fig. NTP visualization with interactive metrics for the modified CIGRE MV Benchmark (using Grafana).
NTP1.html
Notes: The Network Topology Processor acts as the digital map creator of the power distribution network. It reads network data files which are actually the CIM files and builds a complete representation of how all buses, lines, transformers, capacitors, and reactors are connected. This model is then used by other modules such as power flow, state estimation, and voltage control.
NTP module is necessary because before performing any analysis or control action, the system must know the exact network structure. NTP provides this information and ensures that all other modules work with an accurate and updated network model.
(Explain the html)

## Slide 12: Designed ONLF module for Fast, Dockerized Steady-State Analysis
Online Load Flow (ONLF), also known as Operator Load Flow, is a critical function in modern power distribution systems for continuously assessing the steady-state operating condition of the network.
DC power flow: Faster powerflow information.
ONLF1.html
Notes: Traditionally, power flow studies are done offline for pre-planned scenarios. But today’s power grids change rapidly. We need to know what is happening right now. ONLF acts as the brain of advanced Distribution Management Systems. It runs in near real-time, adapting instantly to changes in power demand, network layout, or sudden faults.
To make this run fast enough for real-time monitoring, we couldn't use the traditional, heavy mathematical equations. Instead, we used a simplified approach called the DC Power Flow method.

## Slide 13: Designed EnVVARCO Module Volt-Var Control is a necessity for renewable dominated distribution systems
In RES dominated / active distribution networks, it is necessary to maintain acceptable voltage profiles while efficiently managing reactive power resources , i.e. Volt-Var Control (VVC).
The increasing variability in load patterns and DERs necessitates adaptive control strategies that can respond to both undervoltage and overvoltage conditions in real-time.
Enhanced Volt-VAR Control and Optimization (EnVVARCO) is proposed.
Single line diagram (SLD) of modified CIGRE medium voltage benchmark 15 bus
distribution system
Volt_VAR.html
Notes: Let’s start with why we actually need Volt-VAR Control. The power grid is like a water system. When everyone turns on their appliances at once (heavy load), the electrical 'pressure' drops, causing undervoltage. When demand is very low, the pressure builds up, causing overvoltage, which can damage equipment.
To keep the grid safe, we keep the voltage between 0.95 to 1.05
Now there are certain equipment's which help us to balance the voltages. Capacitors inject power to rise the voltage Reactors absorb power to drop the voltage
Additionally we have tap changing transformers to fine tune the voltage
In a power grid different rating of capacitors and reactors are present.
So in which condition what equipment needs to be turned ON that needs to be identified. And, secondly these equipment's are expensive so constantly flipping might increase wear and tear. Suppose we have 2 capacitors of 5 MVAR and 1 big capacitor of 10 MVAR. And the need is of 10 MVAR increase. So it is better to turn on 1 big capacitor rather than 2 to reduce wear and tear of equipment. For this we have used multi-objective metaheuristic algorithm

## Slide 14: The power system also needs resilience against network faults: NR, AR & SR.
Voltage violations, excessive losses, and delayed fault recovery significantly degrade power quality, system reliability, and customer service continuity.
A hierarchical control framework is developed – spanning steady-state voltage regulation, fast protection and reclosing, and post-fault service restoration.
Auto-Reclosure (AR)
Service Restoration (SR)
Fast fault isolation and transient fault recovery.
Post-fault load recovery using network redundancy
Volt–VAR Control and Network Reconfiguration (NR)
Steady-state voltage regulation and loss-aware topology adaptation.
Notes: So far, we've talked about keeping voltage stable. But real-world power grids face sudden emergencies—like a tree falling on a power line or a short circuit.
Traditionally, utilities use separate systems for everyday voltage control and emergency fault responses. Our goal was to build a single, integrated 'brain' that handles everything automatically, adapting to both normal days and sudden disasters."
To do this, we built a hierarchy made of three distinct modules:
Module 1: EnVVarco which integrates network reconfiguration within it. This is used to regulate the voltage.
Module 2: Auto-Reclosure: If a sudden fault happens, the module 1 is immediately paused so it doesn't make things worse. The module 2 takes over, quickly disconnecting the damaged area. It will try a few times to see if the fault is just a temporary glitch. If it's permanent, it locks the broken section down.
Module 3: Service Restoration: Once the broken section is locked down, this module steps in. It automatically looks for 'backdoors'—alternate power lines—to reroute electricity and restore power to as many nodes as possible."

## Slide 15: Designed NR module : combines EnVVARCO to stabilize system voltages to desired level in RES-rich networks
N.O.
N.O.
N.O.
N.O.
N.O.
N.O.
Grid tie switches (normally open)
Grid tie switch operates
Fig. Bus voltage profiles of the 33-bus distribution network, showing voltage regulation before and after coordinated Volt–VAR control+NR under undervoltage conditions.
Fig. Single line diagram (SLD) of modified IEEE 33 Bus system showing position of grid-ties and their operation
NR.html
Notes: The Network reconfiguration module is an upgraded version of EnVVARCO module. In NR module in addition to capacitors, reactors and tap changing transformers we have additionally considered grid ties. Here also through multi-objective optimization equipment's are selected.
But unlike the EnVVarco module all selected equipment's are not turned on together as it might effect the grid stability. So we have introduced trigger module where the equipment’s are turned on priority based sequence. The 3 Rules of Priority are:
Rule 1: Voltage Sensitivity: The system looks for the device that will make the biggest immediate difference. If turning on a specific capacitor will fix a large portion of the grid all by itself, it gets bumped to the top of the list.
Rule 2: Electrical Distance: Devices located furthest away from the main power source are given higher priority to help boost those struggling outer edges.
Rule 3: The "Heaviest Load" Factor: Areas with heavy electrical demand (like busy neighborhoods or commercial centers) get priority over quiet, low-demand areas.
Once the system calculates the scores and picks the #1 priority device, it turns that device on.
But it doesn’t turn the second one on immediately. It enforces a strict 20-second waiting period. This gives the grid time to "settle" so the new voltage can be measured. If the grid is fixed, it stops. If it still needs help, it moves down the list and turns on the #2 priority device, waits another 20 seconds, and repeats.

## Slide 16: Designed AR+SR modules to tackle power system faults hierarchically and protect the network
N.O.
N.O.
N.O.
N.O.
N.O.
Fault at bus - 15
Circuit breakers (CB) tripped to isolate the fault
N.O.
Grid tie switches (normally open)
Fig. Voltage profile changes at Bus 18 pre-fault, during fault, isolation and stabilizing action post fault isolation with AR, SR.
Fig. Single line diagram (SLD) of modified IEEE 33 Bus system showing position of fault and the CB operation
Bus 18
1.1
0.9
0.7
0.3
0
Time stamp
Voltages in p.u.
Pre fault
during fault
Post-fault
NR_SR_AR.html

## Slide 17: Designed OPF module for smarter DER dispatch for efficient grid operation
Optimal Power Flow (OPF) provides a systematic framework to determine the optimal settings of controllable resources while satisfying the electrical network constraints.
Can reduce real power losses and improve voltage profiles under optimal dispatch conditions, and reduce dependence on the upstream supply, while respecting generator operating limits and network topology.
The acceptable steady-state service-voltage range in distribution systems is commonly taken as 0.95–1.05 p.u., consistent with ANSI C84.1 Range A voltage limits.
Fig. Voltage profile changes for modified IEEE 33 Bus system after optimal dispatch
Under voltages due to non-optimal dispatch
Corrected voltage profiles after optimal dispatch of RES
OPF.html
Notes: Let’s shift gears and talk about power generation. Today’s power grids are adding a lot of local energy sources—like PV plants, wind power plant, and backup diesel generators.
Having this local power is great, but it introduces a new problem. If a wind turbine spins up at maximum speed while solar is peaking, it can actually cause voltage spikes and waste energy. Like a group of talented musicians playing without a conductor, uncoordinated power sources create grid chaos.
To fix this, we implemented an Optimal Power Flow module. Think of OPF as the master conductor of the grid. Its job is to look at all the available local power sources and decide exactly how much power must be extracted from each one.
To test this, we placed three different generators: Solar plant, a Wind turbine, and a dispatchable Diesel generator.
We programmed our OPF module to achieve three strict goals simultaneously:
1. Minimize how much power we have to buy from the main utility grid.
2. Minimize the energy wasted simply traveling through the wires.
3. Ensure the voltage stays perfectly stable for the end-user

## Slide 18: Open-source grid intelligence supports resilient, automated, and sustainable power systems
The presented framework demonstrates how open-source, modular grid intelligence can be deployed in a scalable and reproducible manner.
These approaches may support cost-effective modernization, particularly in systems with high DER penetration and limited infrastructure flexibility.
Future work includes validation across real utility datasets and extended deployment scenarios.
Fig. A brighter, secure and sustainable energy future with open source grid intelligence
Figure courtesy: Google Images
Github Repo
Notes: Concluding lines --- grids facing renewable integration, rural reliability gaps, limited modernization budgets, outage recovery challenges, and DISCOM financial pressure can adopt low-cost, modular automation instead of waiting for vendor implementation. The use of Python, Docker, Grafana, OpenDSS, REST/gRPC APIs, monitoring and logging tools — makes the solutions we proposed potentially portable, reproducible, and scalable from lab pilots to utility environments.
Therefore open source cloud native infrastructure enables reproducibility and deployment. As said Given enough eyeballs, all bugs are shallow.
We would like to test our open source github repos and please give us feedbacks to improve. Thank you.